TENDER FOR PLUMBING WORKS

Included in this pack:

- Job Specification and Return Sheet

- Copy of the Council’s Management of Contractors Policy

- Copy of the Council’s Quotations and Tenders Policy

Please return to the Council:

- The Return Sheet completed with all sections you would like to quote/tender for

- The Contractor Competency Form (found in the Management of Contractors Policy pages 4 and 5)

All paperwork must be received marked ‘Tender for Plumbing Works’, in the Council Office by 4pm on Monday 7th November 2022.

Illogan Parish Council reserves the right to obtain references and complete Companies House or other relevant searches.

If you have any queries,

please do not hesitate to contact the Clerk, Sarah Rimell, using the above contact details.

TENDER FOR PLUMBING WORKS

Replace wall mounted hot water boiler in kitchen and alteration works to the Mains Water Supply in the Changing Facilities, Illogan Park, Paynters Lane, Illogan, Redruth, TR16 4RJ

All works must be completed in line with national guidelines and by suitably qualified and insured persons.  Contractors must have an up to date and valid waste carriers’ licence, appropriate equipment and machinery, be able to satisfy all appropriate health and safety requirements including COSHH, CDM Regulations etc and all appropriate competency certificates.

- Replace water heater

The wall mounted hot water boiler in the kitchen has started to leak and needs to be replaced with a 20litre wall mounted hot water boiler.  There needs to be appropriate isolation and overflow and any other required component.

Please provide details on the model and capacity of the replacement wall mounted hot water boiler.

- Alteration to Mains Water Supply

Project Overview

The existing changing rooms suffer from poor mains cold water flow and pressure.  This is believed to be due to the existing Ø1” supply pipe run below the play park from South West Water’s distribution in Treforthlan Road.

Whilst this supply would be adequate for a standard domestic situation it suffers with low flow during match times when teams are showering.

The new public toilet building has also been added to the changing rooms supply to enable it to operate.

To improve the situation as part of the new parish office works a new Ø32mm Blue MDPE supply pipe has been installed to serve the office and in turn the changing rooms.

This new pipe has been installed below the new tarmac pathway to the rear of the toilet block.

This pipe will be brought to the changing rooms by the existing groundworks contractor for connection to the mains distribution system by the plumbing contractor.

It is planned that the existing mains supply to the changing rooms would now uniquely serve the toilet block and the new Ø32mm will connect to the existing changing room distribution.

Project Works

Refer to Sketch

Once the Ø32mm MDPE is installed and live the plumbing contractor shall perform a flow and pressure test to determine a typical flow rate and supply pressure.

The plumbing contractor shall install a new Ø28mm Cu service pipe rising from the MDPE service into the roof void.  It shall be located adjacent to the existing toilet block pipe housed externally within timber boxing on the western side of the building.  This pipe shall be securely fixed to the wall and fully insulated with a 25mm closed cell foam material.

Upon entering the roof space the Ø28mm Cu pipe shall run towards the centre of the roof void over the entrance lobby, Ø28mm and Ø35mm valved and capped tees shall be provided for the possible future connection of a packaged booster set if deemed necessary or as determined by the flow and pressure tests.  This pump set would be rated at 1.2litres/sec @ 3 Bar.  Break tank to be sized at 1000 litres.  Contractor to provide a separate cost for the supply and installation of a suitable booster pump set and associated electrical connection.

From the future connection point a Ø35mm Cu supply pipe shall be run to the current entry location over the home team changing room.  This new pipe shall connect to the existing roof services at this location to maintain the original pipe sizes and flow.

The existing supply shall be isolated and adapted to provide water to the toilet block.  This shall be achieved by running a new 25mm MDPE supply through the roof space.

All new pipework shall be fully insulated with 25mm wall thickness closed cell material and fully supported along its route.  All pipework shall be fitted with drain valves at low points to enable effective draining of the system.

TENDER FOR PLUMBING WORKS

Return Sheet

| Company Name: |  |
| --- | --- |
| Contact Name: |  |
| Company Address: |  |
| Company Email Address: |  |
| Company Telephone Number(s): |  |
| I confirm that I am able to comply with all Health and Safety Requirements | Y/N |

| Please explain how you will complete the work: |  |  |  |
| --- | --- | --- | --- |
| Please provide details of three other places you complete similar work: |  |  |  |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| Please provide the name and contact details for three referees: |  |  |  |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| Costs: |  |  |  |
| Description |  | Cost | Frequency |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
|  |  | £ |  |
| TOTAL: |  | £ |  |

I confirm that the above information is correct and that I am authorised to submit this return sheet on behalf of the company:

| Name: |  |
| --- | --- |
| Position: |  |
| Signature: |  |
| Date: |  |